## Slide 1: Incedo Lite Product
User manual and technical presentation
V040521

## Slide 2: Features
Database Type: Embedded
Number of Doors: 32
Wired & Aperio On-Line readers
Number of Keyholders: 1,000
Door Modes
Time Profiles
Anti Passback
Emergency Lockdown
Emergency Unlock
V040521
Incedo™ Lite
Notes: Part Numbers – created for all 7 parts (may require additional for bundles with readers)
Pricing – calculations have been completed for Hardware and Readers and awaiting sign off before releasing
  Regional Price list with suggested discount structure to be created
Beta Site due to be installed W/C 4th November for Embedded Solution with the Aperio integration being added in December and Cloud following – we have permission to use this for a cast study
Demo equipment to be ordered for the 4 regions in November once the rebranding exercise has been completed
  Each region will be provided with a controller, reader module(s) and readers
  Copy of the Professional software
  Log in to the Cloud when available
  Note: Training will be provided when handing the equipment over
Plan for control of Professional software needs to be created to protect the regions

## Slide 3: Hardware
The Incedo Lite Access Control System is made up of two core parts – the Cluster Controller & a Reader module. Each system will require at minimum of one Cluster Controller.
These two parts are available in the following variants.
Metal enclosure
Boxed Controller including Cluster Controller, Reader Module, PSU (ROHS/5Amp), Metal enclosure c/w tamper and battery charging circuit
Reader Module, IPS back plate - Boxed Controller Expansion Option
Plastic housing
Cluster Controller, Plastic housing
Reader Module, Plastic housing
V040521
Incedo™ Lite

## Slide 4
The Metal Enclosure comes with a Cluster Controller, a Reader module and PSU.
The Enclosure is expandable up to 4 reader modules allowing a total of 8 doors or 4 doors with in and out readers.
An additional 12V 7Ah Lead-Acid Battery can be added in case of power failure.
Boxed Controller c/w 1 Reader Module c/w 2 Reader Modules
Metal Enclosure with PSU
V040521
Incedo™ Lite

## Slide 5
The Plastic housing version of the Controller is the same as in the Metal Enclosure version only mounted in a Plastic, it does not include a reader module or PSU, these items must be purchased separately.
Controller in Plastic housing with lid removed
*Note. The Plastic housing modules are not designed to be mounted in a Metal Enclosure.
Plastic Housing
V040521
Incedo™ Lite

## Slide 6
12V DC Power
Device RS485 to Slave Controller
Host RS485 to Aperio Hubs
RJ45 Network connection.
Configuration dip switches.
Master = dip switch 2 ON
Slave = dip switch all OFF
*Battery Tag
(remove before connecting power)
Line termination links
Cluster Controller
V040521
Incedo™ Lite
Line termination links
*Power Cycle of the controller when the Battery is not connected or when Flat will result in the System data being removed from the controller.
Battery Type ........................... 1 x 3 V, CR2032, Lithium cell Battery.
Battery Life ............................. 1 Year with Power OFF,
5 years with Power ON,
5 years Storage with Battery Tab in place.

## Slide 7
Two versions available
Reader Module, IPS back plate - Boxed Controller Expansion Option.
Reader Module, Plastic housing - External Expansion
The image shown is the boxed controller version. The plastic mounting differs between the Boxed Controller and Plastic housing version, the PCB stays the same.
Door Connections
Suitable for one door with an IN and OUT reader or two doors with an IN reader only.
Lock output relay. N.O. (Fail Secure) or N.C. (Fail Safe) connections.
Input - Door Position Sensor
Input – Request to Exit
Reader configuration Dip Switch. Default 1 2 3 ON 4 OFF.
Wiegand Reader connection. ASSA ABLOY Pigtail colour coded connections
Up to 4 Reader Modules can be attached to a single Controller
Reader Module
V040521
Incedo™ Lite

## Slide 8: Lock Installation
Incedo™ Lite
Install the MOV as close to the lock as possible.
V040521

## Slide 9
When the number of doors exceeds 8 (4 doors with IN/OUT readers) the system can be expanded by adding additional Cluster Controllers to the “Master” Cluster Controller via a standard RS485 bus*. Each Slave Cluster Controller can handle an additional 4 Reader modules and could be either the metal enclosure or plastic housing depending on the site requirements.
This flexibility allows the system to be design to meet the sites needs without any lose of functionality. Master and Slave Controllers are connected using the Device RS485 connection*.
Slave Cluster Controller
Slave Cluster Controller
Slave Cluster Controller
Slave Cluster Controller(s)
Master Cluster Controller
A
B
SHD
In
Out
In
Out
In
Out
*Standard RS485 rules apply in terms of cable distance and the use of belden cable with 3 conductors available.
*Apply Line termination to the Master Controller and the last Slave Controller on the RS485 bus. See Slide 6.
Max length 1,000m
Architecture for system with over 8 wired doors
V040521
Incedo™ Lite
RS485

## Slide 10
The configuration of Incedo is flexible allowing you to install the equipment that is best suited to the application – The system can be installed in a central location running cables to each door, local to each door with a controller and reader module or a combination of both
Option A – Install a Metal Controller in a central point and run the door cables out
Option B – Install Plastic Controller and Reader Module local to the door and connect controllers via RS485
Wiring Consideration
Incedo™ Lite
Option C – A combination of options A and B.
V040521

## Slide 11
Only the Master Cluster Controller is connected to the Customers Network
Network Configuration options for the Controller are DHCP or Static IP
Only the Master Cluster Controller can be connected to the Aperio RS485 bus
Up to 4 Reader Modules can be connected to a controller, Master or Slave, allowing 4 doors read IN/OUT or 8 doors read IN
Incedo Lite can be configured to manage up to 32 doors (16 doors with IN/OUT readers)
A combination of Wired and Aperio readers can be installed. Combined maximum 32 readers
Slave controllers will run independently if the Master Controller fails
Additional reader modules can be added without powering down the controller allowing uninterrupted use of the system during maintenance
Cluster Controller
V040521
Incedo™ Lite

## Slide 12
Aperio Hubs can only be connected to the RS485 Bus on the Master Controller
Aperio Hubs are connected to the Host RS485 connection
Up to 8 Aperio readers can be paired with an Aperio AH30 Hub
A maximum of 32 Aperio readers can be installed
A maximum of 8 Hubs can be attached to the RS485 Bus
The number of available Aperio doors is reduced by the total number of wired readers attached to the system. Example. If there are 4 wired readers then the number of available doors for use with Aperio is 28
Each Hub requires a Unique address set via dip switch
The RS485 bus requires termination at both ends. The Master controller (see slide 6) and the last Aperio Hub - set via dip switch on the last Hub on the Bus (slide 13 & 14)
Commissioning Aperio devices requires a USB wireless programming dongle, commissioning software and unique Encryption key
Aperio Doors
V040521
Incedo™ Lite

## Slide 13
Connect the AH30 Aperio Hub to the RS485 Host connector on the Master Controller.
Aperio Hubs are connected to the Master Controller only and cannot be connect to a Slave Controller.
Each Hub requires a unique address set using dip switches 1 to 4. Binary addressing dip 1 = address 1, 2 = address 2, 1 & 2 = address 3 etc.
The last hub on the 485 bus requires Pull Up and Pull down resistors and termination set using dip switches 6, 7 and 8
Apply Line termination to the Master Controller for the Host connection on the RS485 bus. See Slide 6.
Aperio Wiring and Dip Switch settings
V040521
Incedo™ Lite

## Slide 14
Connect the AH30 Aperio Hub to the RS485 Host connector on the Master Controller.
Aperio Hubs are connected to the Master Controller only and cannot be connect to a Slave Controller.
Each Hub requires a unique address set using dip switches 1 to 4. Binary addressing dip 1 = address 1, 2 = address 2, 1 & 2 = address 3 etc.
The last hub on the 485 bus requires termination, dip switches 6 and 7.
Aperio AH30 Gen5 Hub Configuration
V040521
Incedo™ Lite
Use the Aperio Programming application to set UID Revers Byte order for Mifare Credentials.
Apply Line termination to the Master Controller for the Host connection on the RS485 bus. See Slide 7.

## Slide 15
Connect the AH20 Aperio Hub to a Weigand module reader connector. Using 8-24v DC, Gnd, Green LED, Red LED, D0 and D1.
Hub dip switch setting 4 ON (reverse Byte order)
Aperio AH20 Wiegand Gen5 Hub Configuration
V040521
Incedo™ Lite
Alternate to Dip Switch 4 setting.
Use the Aperio Programming application to set UID Revers Byte order for Mifare Credentials.

## Slide 16
iCLASS
H10301 26bit, H10302 37bit, H10304 37bit, Corporate 1000 37bit and 48bit.
  Facility code can be enabled for all except the H10302 format.
  The Default format will be iClass H10302. Cards will be available to purchase with the system.
MIFARE
Classic, MIFARE DESFire EV1 (Mifare DESFire CSN limited to 32bit)
Custom Formats
It is possible to setup a custom card mask defining Parity, Ficility Code and Card Number
Card Format
V040521
Incedo™ Lite

## Slide 17
Incedo does not require a host PC or Server.
There is no requirement for software installation.
Incedo Lite is an Embedded Solution accessed via a standard Web Browser
Compatible browsers Google Chrome, Mozilla Firefox, Microsoft Edge and Apple Safari
Access the system direct from a Laptop, PC or Mobile device.
Connect via a static IP address or DHCP.
Configuration
V040521
Incedo™ Lite

## Slide 18
First Option: If you have a DHCP server
Type the following URL in to one of the supported browsers:- http:Incedo
You will be directed to the Incedo Lite login page
The default password is 12345
Connecting for the First Time - DHCP
V040521
Incedo™ Lite

## Slide 19
Second Option: Connect to the Cluster with a Static IP address.
Connect a PC/Laptop directly to the Controller network socket
Type the following IP address in to one of the supported browsers:- 192.168.100.1
You will be directed to the Incedo Lite login page
The default password is 12345
Configuring the systems Network settings see slide 26
To setup your PC/Laptop with a static IP address in the same range as the controller follow the steps on the next slide.
Connecting for the First Time using a Static IP
V040521
Incedo™ Lite

## Slide 20
The Incedo Cluster Controller default IP address is 192.168.100.1
The PC needs a unique IP address in the same range as the controller. Not the same as the controller!
On the Windows PC from the Control Panel
Click Network and Internet followed by Network and Sharing Centre
Select Change adapter settings
Select the appropriate adapter e.g. “Local Area Connection” this will be the adapter the network cable is plugged into. If you are unsure disconnect the network cable and a red X will appear by the appropriate connector.
Right click on the adapter Icon and choose Properties
Double-click “Internet Protocol Version 4 (TCP/IPv4)”
Click “Use the following IP address”
Set the IP Address to 192.168.100.X (X being any available number between 2 and 254.
Set the Subnet Mask to 255.255.255.0.
Click the OK button
Configure your PC with a Static IP address
V040521
Incedo™ Lite

## Slide 21
To Install the Incedo Firmware Upgrade Utility
Double click the Incedo™ Firmware Upgrade Utility.exe
Select Language
Accept the License Agreement
If required tick Create desktop shortcut.
Confirm Install.
Firmware Upgrade Utility - Installation
V040521
Incedo™ Lite

## Slide 22
The utility will auto discover the Incedo Cluster controller when connected via DHCP
Search by IP when using a Static IP address or the default 192.168.100.1
Firmware Upgrade Utility
V040521
Incedo™ Lite

## Slide 23
It is recommended that a Backup is made before making any configuration changes or upgrading firmware in the Cluster Controller.
Select the Controller by clicking on the Device.
Choose the backup Tab.
Choose the Backup icon.
Select a location to store the backup.
To Restore a backup reverse the process.
Firmware Upgrade Utility – Backup/Restore
V040521
Incedo™ Lite
*Note. It is important to ensure the customer is familiar with the backup process. It is the customers responsibility to ensure their data is adequately backed up and stored in a secure and safe location. The consequence of failing to secure the system will result in the reinstallation of all doors, users and credentials.

## Slide 24
Select the Controller by clicking on the Device.
Choose the Firmware Upgrade Tab.
Click Start Upgrade.
If you are reinstalling the same version of firmware or you attempting to roll back to an earlier version you will need to hold the CTRL key down when you click start upgrade.
Firmware Upgrade Utility – Firmware Upgrade
V040521
Incedo™ Lite

## Slide 25
Compatible browsers Google Chrome, Mozilla Firefox, Microsoft Edge and Apple Safari
Enter the URL http://incedo/ or IP address 192.168.100.1 into the browser address bar
Default password 12345
12345
Software Configuration
V040521
Incedo™ Lite

## Slide 26: Live!
V040521
Incedo™ Lite

## Slide 27
About
Application details including Firmware version and Build.
V040521
Incedo™ Lite

## Slide 28
Settings
Network Settings (slide 26)
This will synchronise the Date and Time with the PC
Change Password
Specify Exception days in Calendar for use in schedules
Select the Language
User/Door Access Groups (slide 32)
Use to stream Event output to third party system
Anti Passback settings
Wiegand Reader/Credential format
Logic Functions
V040521
Incedo™ Lite

## Slide 29
Choose the Settings Tab Network option from the Settings menu
The default setting is DHCP
The details show the current Network Configuration
To Configure the system to use a Static IP address untick DHCP
If you are unsure of the network setting please contact the Customers I.T department.
Network Settings
V040521
Incedo™ Lite

## Slide 30
From the Settings TAB
Date & Time: This will synchronise with the PC.
Security: Change the Login Password
Special Days: Additional day type. Add holidays to the calendar.
Language: Select UI language
Settings Configuration
V040521
Incedo™ Lite

## Slide 31: Settings Advanced
Access groups: User/Door Access Groups (See slide 37)
UDP output: Used to stream Event output to third party system
APB Settings: Anti Passback settings Strict or Relaxed.
Wiegand Settings: Wiegand Reader/Credential format. Default H10302
System Rules: Logic Functions. System event to trigger a relay.
V040521
Incedo™ Lite

## Slide 32
Doors
V040521
Incedo™ Lite

## Slide 33
To Establish a list of available doors Click Device Discovery
The Device discovery graphic will appear followed by the number of available doors
Adding Doors
V040521
Incedo™ Lite

## Slide 34
Add Door
Name Door
Select the Device address.
ASSA ABLOY Door reader
Address found on reader Module relay or product Sticker.
Aperio devices
Address found in the Aperio programming application
Adding Doors
V040521
Incedo™ Lite

## Slide 35: Adding Doors
Setting up the Door mode
Locked: Sets the door to a locked state where no users are granted entry.
Card and PIN: A credential and Pin number is required for access*
PAC: Personnel access code. This requires the credential number to be entered at the reader. Aperio uses Maximum 4 digits. (credential as pin)*
On Site Rule: Set a period of time where the door will remain unlocked only after a user with valid access uses their credential
Unlock: Set a period of time where the door will remain unlocked
Reader Address
Set Request to Exit
Normally open/closed
DPS Options
Door held open alarm.
Door relay time setting.
Enable Supervised Input DPS short circuit detection
Reader Buzzer volume setting
V040521
Incedo™ Lite
* When Using a keypad reader with the PAC or Card + Pin mode the user must press the # key following the number

## Slide 36
DPS Input Function
V040521
Incedo™ Lite
Changing the DPS input function makes it possible to change the system behaviour with an external input for example a relay or switch.
Door Sensor Door position information Open/Closed
Disabled Switch off the DPS input
Hold Reader Access Denied for all users
Re-Engage Door Relay Immediately lock door
Emergency Unlock Toggle Unlocks all Doors
Lockdown Toggle Initiate Emergency Lockdown

## Slide 37
Access Groups
Create access groups using the Access Groups option from the Settings Menu
This is where we define a users access rights
Name the access group
Often associated with a group of users
Set the time period for when users assigned to the group will have access
Select the doors that users assigned to the group will have access
V040521
Incedo™ Lite

## Slide 38
Users
V040521
Incedo™ Lite

## Slide 39
Adding Users
User Name details
Profile: Visitor and Employee used in reporting. A profile of Administrator can Override APB
PIN. Personal pin code used for Door mode Card and PIN.
Custom Field: Description free text.
Card Number: Users credential number.
Card Enrolment
Type card number into Field
Use the Button. Select a reader from the list and present the card
Use a USB desktop enrolment reader
V040521
Incedo™ Lite

## Slide 40
User Cards
Card enrolment also available by using the button or USB enrolment reader
Access Group. Defines user Access – What doors a user has access to and when. Access groups are defined under the settings menu (slide 34)
If unmodified the default access group allows access to all doors
Start and End Date. The card validity period. When the card will start working and when it will stop
Suspend card. Temporarily block a card
Adding Users
V040521
Incedo™ Lite

## Slide 41
Anti Passback -APB
V040521
Incedo™ Lite
Anti Passback will work across a single system (site), a controller and slaves controllers.
Doors are not set to APB by default, they need to be enabled for APB in the door configuration.
Only Doors enabled for APB will follow APB rules.
Users with a profile of Employee or Visitor will follow APB rules. Users with an Administrator profile are exempt.
If communication is lost between controllers. Readers connected to Slave controllers will continue to function although they will no longer follow the APB rules.

## Slide 42
Anti Passback
V040521
Incedo™ Lite
Strict Control
Toggle single entry and single exit function. APB readers only.
  After an entry/in reader is used an exit/out reader must be used before an entry/in reader can be used again.
  After an exit/out reader is used an entry/in reader must be used before an exit/out reader can be used again.
Relaxed Control.
Toggle single entry and multiple exit function. APB readers only.
  After an entry/in reader is used an exit/out reader must be used before an entry reader can be used again.
  Any number of exit/out events can occur without reusing an entry/in reader.

## Slide 43
LockDown
V040521
Incedo™ Lite
Use the Lockdown button from the UI or use the Door Position Sensor (DPS) input as a trigger
If you initiate a lockdown it will do two things.
Lock all doors that are following an open schedule.
Deny access to all users on all doors. i.e. all readers/access is blocked.
If you initiate a lockdown using a physical input you can only reset by using the physical input. The software will not allow you to revert to a normal state.
The physical input uses a DPS input so if you have a read in/out door you can use the spare DPS input.
If you are only using read in doors then you will either need to sacrifice a reader port or at least steal the DPS input from that door.

## Slide 44
Emergency Unlock
V040521
Incedo™ Lite
Use the Emergency Unlock button from the UI or use the Door Position Sensor (DPS) input as a trigger
If you initiate an Emergency Unlock all doors will immediately Unlock
If you initiate an Emergency Unlock using a physical input you can only reset by using the physical input. The software will not allow you to revert to a normal state.
The physical input uses a DPS input so if you have a read in/out door you can use the spare DPS input.
If you are only using read in doors then you will either need to sacrifice a reader port or at least steal the DPS input from that door.

## Slide 45
System Rules
V040521
Incedo™ Lite
A system rule allows a System Event to trigger one or all door relays for a set duration
Trigger Source – The door related to the Trigger Event
Trigger Event – The required Event to trigger the relay to change state
Relay – The door relay that will change state
Duration – The length of time the before the relay resets

## Slide 46
Reports
Door Events
Hardware Status
Changes made to the software
Available when using APB
Shows the first and last user door event. Requires Entry Exit readers
Hardware repot showing devices attached to the system
V040521
Incedo™ Lite

## Slide 47
Q&A
V040521
Incedo™ Lite

## Slide 48: Thank you
assaabloy.com
V040521